## 835-2019-80763075
Batch | EUDKVE-00922913
Sagsnavn | Bjerregrav Vandværk - Vandværket
Sagsnummer/lokalitetsnr
Udtagningsdato | 2020-02-06 10:25
Modtaget på laboratoriet | 2020-02-06 23:53
Rapport (seneste rapportrevision) | 21-02-2020/AR-20-CA-00922913-01
Prøvenummer | 80763075
Prøve mærke | Afgang vandværk
DGUnr
Komponent | Resultat | Enhed | DL | Metode
Farvetal, Pt | 1.2 | mg Pt/l | 1 | DS/EN ISO 7887:2012, metode C
Turbiditet | 0.07 | FNU | 0.05 | DS/EN ISO 7027-1: 2016
Coliforme bakterier 37°C | < 1 | MPN/100 ml | 1 | Colilert Quanti Tray
Escherichia coli | < 1 | MPN/100 ml | 1 | Colilert Quanti Tray
Enterokokker | < 1 | CFU/100 ml | 1 | ISO 7899-2:2000
Kimtal ved 22°C | 4 | CFU/ml | 1 | ISO 6222:1999
Hårdhed, total | 10 | °dH | 0.1 | SM 3120 ICP-OES
Calcium (Ca) | 68 | mg/l | 0.5 | SM 3120 ICP-OES
Magnesium (Mg) | 3.3 | mg/l | 0.1 | SM 3120 ICP-OES
Ammonium (NH4) | 0.0065 | mg/l | 0.005 | SM 17. udg. 4500-NH3 (H)
Nitrit | < 0.001 | mg/l | 0.001 | SM 17. udg. 4500-NO2 (B)
Nitrat | < 0.3 | mg/l | 0.3 | SM 17. udg. 4500-NO3 (H)
Aggressiv kuldioxid | < 2 | mg/l | 2 | DS 236:1977
Hydrogencarbonat | 108 | mg/l | 3 | DS/EN ISO 9963
Sulfid-S | < 0.02 | mg/l | 0.02 | DS 278:1976 auto
NVOC, ikke-flygtigt org. kulstof | 0.45 | mg/l | 0.1 | DS/EN 1484
Jern (Fe) | 0.01 | mg/l | 0.01 | DS/EN ISO 17294m:2016 ICP-MS
Mangan (Mn) | < 0.002 | mg/l | 0.002 | DS/EN ISO 17294m:2016 ICP-MS
Methan | < 0.005 | mg/l | 0.005 | M 0066 GC-FID
PFBA (Perfluorbutansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFBS (Perfluorbutansulfonsyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFPeA (Perfluorpentansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFHxA (Perfluorhexansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFHxS (Perfluorhexansulfonsyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFHpA (Perfluorheptansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFOA (Perfluoroktansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFOS (Perfluoroktansulfonsyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
6:2 FTS (Fluortelomersulfonat) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFOSA (Perfluoroktansulfonamid) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFNA (Perfluornonansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
PFDA (Perfluordekansyre) | <0.001 | µg/l | 0.001 | DIN38407-42 mod. LC-MS/MS
Sum PFAS | # | µg/l | 0 | DIN38407-42 mod. LC-MS/MS
Pentachlorphenol | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
2,4-dichlorphenol | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
2,6-dichlorphenol | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
2,6-DCPP (2-(2,6-dichlorphenoxy-propionsyre)) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
2,6-dichlorbenzosyre | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
4-CPP | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Alachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Aldrin | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
AMPA (Aminomethylphosphorsyre) | < 0.01 | µg/l | 0.01 | M 8270 LC-MS/MS
Atrazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, 2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, deisopropyl-2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl-2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desethyl-desisopropyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, desisopropyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Atrazin, didealkyl-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
BAM (2,6-dichlorbenzamid) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Bentazon | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chloridazon, desphenyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chloridazon, methyl-desphenyl- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Chlorothalonil-amidsulfonsyre (CTA) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Desethyl-terbutylazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dichlobenil | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
Dichlorprop (2,4-DP) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dieldrin | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
Dimethachlor ESA (CGA 354742) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Dimethachlor OA (CGA 50266) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Diuron | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Ethylenthiourea (ETU) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Glyphosat | < 0.01 | µg/l | 0.01 | M 8270 LC-MS/MS
Heptachlor | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
Heptachlorepoxid (sum af cis+trans) | < 0.01 | µg/l | 0.01 | M 0352 GC-MS
Hexazinon | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
MCPA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Mechlorprop (MCPP) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl CGA 108906 | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl CGA 62826 | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metalaxyl-M | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metazachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metazachlor OA (479-4) | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-desamino | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-desamino-diketo | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Metribuzin-diketo | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
N,N-dimethylsulfamid | 0.015 | µg/l | 0.01 | M 0336 LC-MS/MS
Propachlor ESA | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Simazin | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Simazin, 2-hydroxy- | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
4-nitrophenol | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
1,2,4-triazol | < 0.01 | µg/l | 0.01 | M 0336 LC-MS/MS
Akkrediteret prøvetagning | Ja |  |  | DS ISO 5667-5,DS/EN ISO 19458,MST - Drikkevand. Manual for prøvetagning (v4, 201 N/A
pH | 7.8 | pH |  | DS/EN ISO 10523
Prøvetagning efter flush | Udført |  |  | DS ISO 19458,DS ISO 5667-5,MST - Drikkevand. Manual for prøvetagning (v4, 201 N/A
Vandtemperatur | 8.2 | °C |  | DS/EN ISO 19458
Ledningsevne ved 20°C | 420 | µS/cm | 15 | DS/EN 27888:2003 (ved 20°C)
Iltindhold | 8 | mg/l | 0.1 | DS/EN ISO 5814